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Code Compliance Summary

	DETAILS

	Property Address:
	80 Byron Street Sydenham

	Consent Issue Date:
	Building Consent Number:
	Project Description:

	22/08/2017 10:32:04 AM
	BCN/2017/2013
	Addition to Factory - New Offices, Meeting and Store Room

	Building level:   ☐ R1    ☐ R2    ☐ R3    C1   ☐ C2   ☐ C3

	Vetting officer:
	Name:  
	Tracey Atherton
	Date Vetting officer Pre-acceptance completeness check started:*
	2021-07-19

	Property file ordered?
	☐ Yes    N/A - e-copy in TRIM
	Date Property file ordered (if applicable):
	

	CC Assessor:
	Name:  
	Cindy Xia
	Date CC Assessor process started:
	23/07/2021

	
	Competency:  
	R1-C3
	
	

	Historic consents process only

	Senior Building Inspector:
	Name:  
	
	Building Inspector:
	Name:  
	

	
	Competency:  
	
	
	Competency:
	

	Risk Level:  
	☐ Low
☐ High
	Reason for level decision:
[Note: if a compliance schedule review is required] 
	



	[image: ]
	
	
	
	
	
	
	
	
	Key for abbreviations to answering processing questions:

	
	Phone 1st:
	Agent
	
	
	
	Y
	Yes - the application meets the full intent of the question. Provide comment as appropriate.

	
	
	Owner
	
	
	
	N
	No - the application does not meet the full intent of the question. Provide comment as appropriate.

	
	
	
	
	
	
	
	
	
	N/A
	Not applicable - the question is not applicable to this application. Provide comment as appropriate.
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	[bookmark: Sec1]SECTION 1: VETTING & ALLOCATION INITIAL COMPLETENESS CHECK

	Application for Code Compliance:
All required sections of application form completed and signed? 
[If owner has changed Certificate of Title is required]
	  Y  
	21/1017547
CD – 16/07/2021

	If the proposed building work includes 'restricted building work' has an appropriate 'records of work' been provided for all of the proposed 'restricted building work' by each LBP, Architect or Engineer?
[Note received ROWs below and lapse in Connect]
	  N/A  
	



	Type of Restricted Building Work:
	LBP Licence Class:
	LBP Name and Licence Number:
	LBP Rego Current?
	TRIM Ref:

	select 
	
	select 
	
	☐
	

	select 
	
	select 
	
	☐
	

	select 
	
	select 
	
	☐
	

	select 
	
	select 
	
	☐
	

	select 
	
	select 
	
	☐
	

	select 
	
	select 
	
	☐
	

	select 
	
	select 
	
	☐
	

	select 
	
	select 
	
	☐
	

	select 
	
	select 
	
	☐
	

	select 
	
	select 
	
	☐
	



	Have Energy Certificates been provided?
(e.g. House; Heating, Gas)
[Lapse in Connect and record HPRM ref]
	  Y  
		CDOC-EW01 
	Energy work certificate - electrical
	Accepted
	12 May 2020
	TRIM://20/579041 
	TRIM://20/579041 Accepted - Document(s) can be relied on as author is qualified and holds a current registration - Tracey Atherton - 2020-05-12
		[image: ]










	[bookmark: Sec1a]SECTION 1a:  INITIAL COMPLETENESS CHECK DECISION

	I confirm that the Vetting & Allocation initial completeness checks have been completed and that the Code Compliance Certificate application is:
	ACCEPTED

	☐ 	NOT ACCEPTED - the reason for non-accepted is:
	

	Signed by the Vetting & Allocation Officer and also confirms that checks are completed and that all relevant information in Section 11 (marked with an *) is contained in the building consent file :

	[image: ]
	Date:
	2021-07-19

	RECORD ANY PREVIOUS "NOT ACCEPTED" DECISIONS - If N/A please    Not Applicable  

	Date
	V&A Officer
	Reason for non-acceptance

	
	
	

	
	
	




	Code Compliance Assessor to complete – insert relevant data from 025 CCC Statement of Compliance:

	Minor Variations:
	Details:   

	 
	Minor Variation: BCN/2017/2013

	Received date
	Decision
	Decision date
	To be invoiced

	23 Oct 2019
	Amendment required
	23 Oct 2019
	$0.00

	Total Minor Variation processing fee
	$0.00

	Minor Variation invoiced amount
	$0.00

	Total to be invoiced
	$0.00


 

	Amendments:
	Details:   

		Amendments: BCN/2017/2013

	Consent number
	Status
	Description

	BCN/2017/2013/A
	Completed
	Amendment 1 - Addition of concrete wall, store room replaced with office space, office partition walls removed, 1 skylight location change, addition of heat pumps, drainage plumbed to sink wastes, hallway extended, interior office windows added, perimeter strip drains reduced to entry doors only, cladding change

	BCN/2017/2013/B
	Completed
	Amendment 2 - change to floor plan, emergency lighting and backflow prevention device




	Other Consents:
	Details:   

		Address related building consents: BCN/2017/2013

	Consent number
	CCC issued
	Status
	Description

	BCN/1994/3440
	09 Aug 1996
	Completed
	Sign (hall shopfitting) miscellaneous freestanding sign (hall shopfitting)- Historical Reference CON94003859

	BCN/2010/8559
	16 Oct 2013
	Completed
	REPLACE ROLLER DOOR WITH FIRE WALL- Historical Reference ABA10107578




	Section 37 required:    Resource Consent Issued  
	Details:   

		Section 37: BCN/2017/2013

	Type
	Lapsed date
	Lapsed
	Status

	Section 37 Other Consents Required
	13 Apr 2017
	Lapsed
		[image: ]







	Resource Consents:
	Details:   

	Processing complete

	Development Contributions:    Paid  
	Details:   DC invoice paid 14/05/2020: DCs of $5,597.90 including GST has been paid.Receipt #248762Kelly**no associated consent**

	Warnings and Bans:    No       
	Details:   

	

	Certificates for Public Use:    No       
	Details:   

	  
	

	Compliance Schedule required:    New  
	BWOF Officer Name:
	Ponferrada, Noemi <Noemi.Ponferrada@ccc.govt.nz>

	
	BWOF Number
	 WOF56989 

	General Comments: [Include any applicable Connect memo’s]

	



	[bookmark: Sec2]SECTION 2: INSPECTIONS – insert ‘Inspection status’ and table from 025 CCC Statement of Compliance: [if a Staged Consent, include all tables]

		Inspections status: BCN/2017/2013

	Inspection type
	Description
	Result
	Date
	Status

	210 - Final Inspection
	Actual
	Pass
	16 Jul 2021
		[image: ]
	




	201 - Pre Pour Foundation
	Not required
	N/A
	09 May 2019
		[image: ]
	




	203 - Pre Pour Floor
	Not required
	N/A
	09 May 2019
		[image: ]
	




	205 - Pre Line (Pre Line including Plumbing)
	Actual
	Pass
	21 Nov 2019
		[image: ]
	




	208 - Drainage
	Not required
	N/A
	21 Nov 2019
		[image: ]
	




	209 - Pre Stop (Pre Stopping)
	Actual
	Pass
	26 Nov 2019
		[image: ]
	




	215 - Building and Sill Wrap or Cavity Batten
	Not required
	N/A
	24 Sep 2019
		[image: ]
	




	217 - Pre Roof
	Actual
	Pass
	13 Sep 2019
		[image: ]
	




	221 - Blockwork (Block Work Construction)
	Not required
	N/A
	07 Feb 2020
		[image: ]
	




	251 - Foundation or Slab
	Actual
	Pass
	22 May 2019
		[image: ]
	




	252 - Drainage
	Actual
	Pass
	26 Nov 2019
		[image: ]
	




	253 - Pre Cladding
	Actual
	Pass
	21 Nov 2019
		[image: ]
	






	Inspection history: BCN/2017/2013

	Click for the Inspection Reconciliation Report

	Inspection date
	Type
	Result
	Duration (hrs)

	09 May 2019
	201 - Pre Pour Foundation
	N/A
	0.00

	09 May 2019
	203 - Pre Pour Floor
	N/A
	0.00

	22 May 2019
	251 - Foundation or Slab
	Pass
	0.75

	13 Sep 2019
	217 - Pre Roof
	Pass
	0.75

	24 Sep 2019
	215 - Building and Sill Wrap or Cavity Batten
	N/A
	0.00

	25 Sep 2019
	253 - Pre Cladding
	Fail
	1.00

	10 Oct 2019
	205 - Pre Line (Pre Line including Plumbing)
	Fail
	0.75

	21 Nov 2019
	208 - Drainage
	N/A
	0.00

	21 Nov 2019
	205 - Pre Line (Pre Line including Plumbing)
	Pass
	0.75

	21 Nov 2019
	253 - Pre Cladding
	Pass
	0.75

	26 Nov 2019
	252 - Drainage
	Pass
	0.75

	26 Nov 2019
	209 - Pre Stop (Pre Stopping)
	Pass
	0.75

	07 Feb 2020
	210 - Final Inspection
	Fail
	0.75

	07 Feb 2020
	221 - Blockwork (Block Work Construction)
	N/A
	0.00

	11 May 2020
	210 - Final Inspection
	Pass
	0.50

	16 Jul 2021
	210 - Final Inspection
	Pass
	0.50







	[bookmark: Sec3]SECTION 3: INSPECTION HISTORY
	Y / N
	Comments, Dates, Details

	All required inspection types identified as passed:
	  Y  
	

	Total Prepaid Inspections:
	
	

	Total Inspections Completed:
	
	

	Total Fee:
	  Owing
	$
	255

	Additional Comments: [Please list TRIM links to Cost Breakdown information and Inspection Calculations documentation]

	

	Modification of durability [Performance requirement B2.3.1] – If N/A please     Not Applicable  

	Substantial completion of building work:  16/07/2021
[Refer to audit or final inspection report confirming substantial completion date i.e. month & year]



	[bookmark: Sec4]SECTION 4: DOCUMENTATION SUMMARY

	Documentation Status:
	Action / TRIM link and notes:

	Construction Statement – B-083
	Action:    Not required

	
	TRIM link and Assessor Notes: 
	

	Plumbing – B-084:
	Action:    Accepted by CC assessor

	
	TRIM link and Assessor Notes:  
	TRIM://20/576877 ACCEPTED BCN, address, all complies, signed by Keith Foster, active Plumbing, Reg20315 confirmed, Signed and dated- Cindy Xia15/05/2020

	Surveyors Certificate (Siting, HIRB, FFL):
	Action:    Accepted by CC assessor

	
	TRIM link and Assessor Notes:
	Building location certificate: Provide a B-081 certificate from a registered professional surveyor or a licenced cadastral surveyor.

TRIM://20/410836 ACCEPTED BCN and Address, form complete, complies with building consent plans, author adrian cowie, No license number, website envidence, signed and dated - Please check it by inspector - Cindy Xia 30/04/2020

	Construction Review (PS4 and Site Inspections):
[If applicable, record consultant name]
	Action:    Accepted by CC assessor

	
	TRIM link and Assessor Notes:  
	Construction Monitoring: Provide all site inspection records and a PS4 from your nominated structural
consultant [Torlesse Structural] stating that all the necessary aspects of the design has been
incorporated into the Building. This includes the following  work:
· Excavation (subgrade beneath foundation footprint) – by Geotechnical engineer
· Foundations before casting
· Concrete block walls after reinforcing but before grouting
· Structural steelwork after erection
· Connections between structural components

TRIM://19/1255274 Page 10-12

TRIM://20/128557 ACCEPTED PS4 from Troless Structural Ltd, notes BCN, Amendment number, address, CM3, B1, signed & dated byLong, William Julius CPEng 231242 verified current, site reports attached – Cindy Xia 19/02/2020

	Façade inspections (PS4 and Site Inspections):
[If applicable, record consultant name]
	Action:    Not required

	
	TRIM link and Assessor Notes:
	

	Drainage Systems (As built):
	Action:    Accepted by CC assessor

	
	TRIM link and Notes:  
	TRIM://20/576877 ACCEPTED As-built plan – Josh Eady, Reg#22552 – Cindy Xia 15/05/2020

	Exterior Cladding (PS3):
[If applicable, record the system]
	Action:    Not required

	
	TRIM link and Notes:  
	

	Membrane – External, e.g., Roof and Decks (PS3):
	Action:    Not required

	
	TRIM link and Notes:  
	

	Membrane – Internal, e.g., Shower (PS3):
	Action:    Not required

	
	TRIM link and Notes:
	

	As-built Truss Design:
	Action:    Not required

	
	TRIM link and Notes:  
	

	Penetrations through fire separations:
	Action:    Not required

	
	TRIM link and Notes:  
	TRIM://21/1056647 Email from agent:” I can confirm there were no penetrations going thru fire cells in this build.”

[image: ]


	Intumescent paint:
	Action:    Not required

	
	TRIM link and Notes:
	

	Potable water test certificate (not NUO):
[If applicable, record consultant name]
	Action:    Not required

	
	TRIM link and Notes:
	

	On-site disposal systems (PS3):
	Action:    Not required

	
	TRIM link and Notes:
	

	Pressure sewer system (B082):
	Action:    Not required

	
	TRIM link and Notes:
	  

	Section 77 Registered:
	Action:    Not required

	
	TRIM link and Notes:
	  

	Staged Consent:
[If applicable, ensure that the RFI references this]
	Action:    Not required

	
	TRIM link and Notes:
	  

	Other: 
	
	Action:  select 

	
	
	TRIM link and Notes:
	

	Other: 
	
	Action:  select 

	
	
	TRIM link and Notes:  
	

	Other: 
	
	Action:  select 

	
	
	TRIM link and Notes:
	

	Other: 
	
	Action:  select 

	
	
	TRIM link and Notes:
	

	Other: 
	
	Action:  select 

	
	
	TRIM link and Notes:  
	

	Other: 
	
	Action:  select 

	
	
	TRIM link and Notes:
	

	Other: 
	
	Action:  select 

	
	
	TRIM link and Notes:
	

	Notes:

	

	Only the above producer statements have been considered for reliance. If other producer statements have been provided voluntarily, they will be saved in the consent file in TRIM, but not reviewed or relied upon.



	[bookmark: Sec5]


SECTION 5: DOCUMENTATION SUMMARY – SPECIFIED SYSTEMS – If n/a please select 

	Documentation Status:
	Action / TRIM link / Notes:

	1 Automatic systems for fire suppression:
	- (PS3):
	Action:    Not required

	
	TRIM link and Notes: 
	

	- (Certificate of Compliance):
	Action:    Not required

	
	TRIM link and Notes: 
	  

	2 Automatic or manual emergency warning systems for fire or other dangers:
	- (PS3):
	Action:    Not required

	
	TRIM link and Notes: 
	

	- (Certificate of Compliance):
	Action:    Not required

	
	TRIM link and Notes: 
	  

	3/1) Automatic doors:

	Action:    Not required

	
	TRIM link and Notes: 
	

	3/2) Access control doors:

	Action:    Not required

	
	TRIM link and Notes: 
	

	3/3) Automatic fire doors:
	Action:    Not required

	
	TRIM link and Notes: 
	

	4 Emergency lighting systems (PS3)
	Action:    Accepted by CC assessor

	
	TRIM link and Notes: 
	TRIM:// 21/1015483 ACCEPTED PS3 EML,  address, BCN, description and scope acceptable, Code clauses F6, F8, indicated, relevant qualification given E257447  signed by Tim Davies dated 20/05/2020 – Cindy Xia15/05/2020

	4 Emergency lighting systems (PS4)
	Action:   Accepted by CC assessor

	
	TRIM link and Notes: 
	Emergency lighting - with PS4 for F6 from Cosgroves

PS1 AMENDMENT 2 -  TRIM://20/801376

TRIM:// 21/1056647 ACCEPTED PS4 from Cosgroves Ltd, notes BCN, Amendment A,B address, CM2, F6 & F8 (Part), signed & dated by Stephen Page CPEng 216143 verified current – Cindy Xia 27/07/2021

	5 Escape route pressurisation systems:
	Action:    Not required

	
	TRIM link and Notes: 
	

	6 Hydrant System/Riser mains:
	Action:    Not required

	
	TRIM link and Notes: 
	

	7 Automatic backflow preventers connected to potable water supply:
	Action:    Accepted by CC assessor

	
	TRIM link and Notes: 
	TRIM:// 21/1015483 ACCEPTED IQP Test report. Address, Location: Service office, make Apollo, size: 20mm, Model number: DCAUCF4A, Serial #985136, Signed by IQP 886 Matt Boot confirmed dated 13/07/2021 – Cindy Xia 23/07/2021

	8/1, 8/2, 8/3 Lifts, Escalators, travelators, or other systems for moving people within buildings:
	Action:    Not required

	
	TRIM link and Notes: 
	

	9 Mechanical ventilation or air conditioning systems (HVAC):
	Action:    Accepted by CC assessor

	
	TRIM link and Notes: 
	TRIM:// 21/1016728 ACCEPTED HVAC As-built plan – Cindy Xia 23/07/2021

TRIM://20/576877 ACCEPTED PS3 HVAC,  address, BCN, description and scope acceptable, Code clauses G4,indicated, relevant qualification givenE257447  signed by Tim Davies dated29/01/2020 – Cindy Xia15/05/2020

	10 Building maintenance units providing access to the exterior and interior walls of buildings:
	Action:    Not required

	
	TRIM link and Notes: 
	

	11 Laboratory fume cupboards:
	Action:   Not required

	
	TRIM link and Notes: 
	

	12/1, 12/2 Auto loops or other assistive listening systems:
	Action:    Not required

	
	TRIM link and Notes: 
	

	13/1, 13/2 Natural/Mechanical smoke control systems, smoke curtains:
	Action:    Not required

	
	TRIM link and Notes: 
	

	14/1) Emergency power systems:
	Action:   Not required

	
	TRIM link and Notes: 
	

	14/2) Signs relating to, a system or feature specified in any of clauses above: 
	Action:    Accepted by CC assessor

	
	TRIM link and Notes: 
	Checked by final inspection -TRIM:// 21/1015483 Accepted Photos for no storage above 3M.

	15/1) Systems for Communicating spoken information intended to facilitate evacuation: 
	Action:    Not required

	
	TRIM link and Notes: 
	

	15/2) Final exits(as defined by clause A2 of the Building Code); and
	Action:    Accepted by CC assessor

	
	TRIM link and Notes: 
	Checked by final inspection

	15/3) Fire separations (as so defined); and
	Action:    Not required

	
	TRIM link and Notes: 
	

	15/4) Signs for communicating information intended to facilitate evacuation; and
	Action:    Accepted by CC assessor

	
	TRIM link and Notes: 
	Checked by final inspection

	15/5) Smoke separations (as so defined):
	Action:    Not required

	
	TRIM link and Notes: 
	

	Fire Engineer PS4:
	Action:    Accepted by CC assessor

	
	TRIM link and Notes: 
	TRIM:// 21/1015483 ACCEPTED PS4 from FireForce Ltd  notes BCN, Amendment A, address, CM2, C3, C4, signed & dated by Will Tsai CPEng 1011344 verified current, site reports attached – Cindy Xia 23/07/2021

TRIM://20/576877 ACCEPTED Letter from FireForse – inspection records – Cindy Xia 15/05/2020

	Other: 
	
	Action:  select 

	
	
	TRIM link and Notes: 
	

	Other: 
	
	Action:  select 

	
	
	TRIM link and Notes: 
	

	Other: 
	
	Action:  select 

	
	
	TRIM link and Notes: 
	

	Other: 
	
	Action: select 

	
	
	TRIM link and Notes: 
	

	Other: 
	
	Action:  select 

	
	
	TRIM link and Notes: 
	

	Other: 
	
	Action:  select 

	
	
	TRIM link and Notes: 
	

	Compliance Schedule Review:

	  Completed  

	Documentation Notes:

	 2021-07-29 – CS review completed. All documentations were supplied.

CS and CSS issued under WOF/2020/5827. 

	Only the above producer statements have been considered for reliance. If other producer statements have been provided voluntarily, they will be saved in the consent file in TRIM, but not reviewed or relied upon.



	[bookmark: Sec6]SECTION 6: STATEMENT BY PERSON(S) WITH A REGULATION 18 QUALIFICATION

	I have reviewed and verified the above construction documentation (Section 4 and Section 5), and I am satisfied they demonstrate the building work complies with the building consent.

	Notes:  I have reviewed the auditor’s notes in regards to received documentation and I believe that ccc can now be issued.  
	Signature(s):   [image: ]
Jacob Burns
Acting Senior Building Inspector 


 
	[bookmark: Sec7charges]SECTION 7: CHARGES

	Notice to Fix -  
	       n/a                                       
	occurrences:
	$ 
	  

	CCC Building Inspections
	    21/1045411                                          
	occurrences:
	$ 
	255  

	Code Compliance Re Application Fee (S95):
	$ 
	

	Code Compliance Additional processing
	       21/1059808         
	
	$
	628.30

	Reminder: 	Include 30 minutes additional processing time for issuing the Code Compliance Certificate
	Include 60 minutes additional processing time for issuing the Compliance Schedule

	Minor Variation
	        n/a                   
	occurrences:
	$ 
	  

	Amendment to modify building code clause B2 – Durability (deposit)
	         n/a                
	$ 
	  

	Other:                                       
	        n/a                 
	$ 
	

	  Total Fees Outstanding  
* Code Compliance must be issued before Refunds are processed
* Funds owed/refunded may be adjusted in the event of a failed final inspection
	$ 
	883.20

	Additional Comments: [Please list TRIM links to any additional Chargeable Services and Processing Reconciliation documentation]

	  



 
	[bookmark: Sec8inv]SECTION 8: INVOICING / REFUNDS

	Invoice / Credit Note Number:
	Amount:
	Type:
	Date Sent:
	Sent to:
	Date Paid:
	TRIM Ref: [Insert TRIM link to Invoice / Credit Note]

	219631
	$883.20
	Inspection (additional)

CCC additional
	27/07/2021
	AGENT
	02/08/2021
	  

	
	
	
	
	
	
	  

	
	
	
	
	
	
	  

	
	
	
	
	
	
	  

	
	
	
	
	
	
	  



	[bookmark: Sec9add]SECTION 9: ADDITIONAL COMMENTS

	Officer’s Note:

	



	[bookmark: Sec10Final]
SECTION 10: FINAL CODE COMPLIANCE APPLICATION SIGN OFF

	Matters for consideration by building consent authority in deciding to issue a code compliance certificate
DECISION – Select yes if you agree, or no if you disagree with the applicable statement below. Select N/A for the statement that is not applicable
  Yes   : Section 94 (for building consents granted under the Building Act 2004) 
On the basis of the satisfactory completion of inspections and that all the construction documentation requested with the building consent has been provided and verified by a person with a regulation 18 qualification, I, on behalf of the Christchurch City Council, am satisfied on reasonable grounds that the building work complies with the building consent and that in a case where a compliance schedule (or an amendment to an existing compliance schedule) is required as a result of the building work, the specified systems in the building (or that are being altered in, or added to, the building in the course of the building work) are capable of performing to the performance standards set out in the building consent. Consideration also has been made that the requirements of section 94 (2), (3) and (4) have been met.
OR

  N/A   :  Section 436 (for building consents granted under the Building Act 1991)
On the basis of the satisfactory completion of inspections and that all the construction documentation requested with the building consent has been provided and verified by a person with a regulation 18 qualification, I, on behalf of the Christchurch City Council, am satisfied that the building work concerned complies with the building code that applied at the time the building consent was granted.

	Issue of code compliance certificate or refusal to issue code compliance certificate
  Yes   :  Section 95 Issue of code compliance certificate
On the basis of the decision above the code compliance certificate must be issued by Christchurch City Council on the prescribed form on payment of any fees and charges imposed by the building consent authority under section 219 or 240.
OR
  N/A   :  Section 95A Refusal to issue code compliance certificate
On the basis of the decision above the Christchurch City Council refuses to issue a code compliance certificate, and must give the applicant written notice of the refusal; and the reasons for the refusal. 

	Name:   
	Cindy Xia  

	Date:   
	02/08/2021

	Select option above (issue or refusal) and sign:
	

	
	Signature: 

	[image: ]

	Weiwei Xia

	Code Compliance Assessor

	02/08/2021 12:44 pm



  



	[bookmark: Sec11Sup]SECTION 11: SUPERVISION - If n/a please   Not Applicable  

	
	Comments: 
	

	
Record details of supervision by competent Code Compliance Assessor where building category is above or outside Assessor's competency level.
Provide competent officer’s name and date of ‘sign-off’.
	

	
	Signature:   



	[bookmark: Sec12CCA]SECTION 12: CODE COMPLIANCE ASSESSOR FINAL PROCEDURES CHECKLIST:
CONFIRMATION THAT ALL RELEVANT INFORMATION IS CONTAINED IN THE BUILDING CONSENT FILE
	Located: Y / N / NA

	* B-011 Application for Code Compliance Certificate (Form 6)
	  Y  

	* Record of Work(s) by licensed building practitioners (Form 6A, B, C)
	  N/A  

	* Energy works certificates
	  Y  

	B-013 Application for Certificate for Public Use (Form 15)
	  N/A  

	B-450 Certificate for Public Use (Form 16)
	  N/A  

	B-440 Notice to Fix (Form 13)
	  N/A  

	B-460 Compliance Schedule statement (building warrant of fitness) (Form 10)
	  N/A  

	B-461 Section 1 Compliance Schedule
	  N/A  

	Dangerous/EQ prone/Insanitary Building notices (section 124 notices)
	  N/A  

	Producer statement construction (PS3) / Producer statement construction reviews (PS4)
	  Y  

	Inspections records and evidence
	  Y  

	Minor variation documentation
	  N/A  

	Summary of written complaints
	  N/A  

	B-006 Application for amendment to building consent for modification of durability periods to clause B2.3.1
	  N/A  

	B-410 amended building consent subject to a modification of B2.3.1
	  N/A  

	B-140 Notification of Waiver or Modification of the Building Code
	  N/A  

	Copy of invoices
	  N/A  

	All email/letter/faxed correspondence relative to the individual consent
	  Y  

	Staged building consents – All stages completed
	  Y  

	B-451 Code Compliance Certificate (Form 7)
	  Y  

	FINAL TASK CHECKLIST:
	

	Have all workflows been completed in connect and final administration completed
	  Y  

	All CCC documents have been converted to PDFs
	  Y  

	All building consent file documents are made 'public' and 'finalised'
	  Y  

	If the application is commercial structural strengthening/upgrade related, email a copy of the B451 and relevant PS4 to DEEs@ccc.govt.nz 
	  N/A  

	If the application includes a pressure sewer system, email the BCN, address and As-Built drainage trim reference to asset.handover2@ccc.govt.nz 
	  N/A  



	
Confirmed by the Code Compliance Assessor that all relevant information in Section 11 (not marked with an *) is contained in the building consent file:


	Name:	
	[bookmark: _GoBack]Cindy Xia

	Date:
	02/08/2021
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Bdsting fre/smoke separations - There are fwo existing rooms within the
warehouse, one vih access fo fhe storage area above e room and one
Vithout access. The room with access fo the storage area above fhe room is
‘considered a mezzanine floor. We belleve fhese 1o rooms have nof been
‘consented. Refer fo picfure A and B n the aftached fie skefch.

The base building fr report prepared by Cosgroves, ssue B, November 2016
nstructs the removal of al mezzanine floor. Eiher remove fhe mezzanine
floor o alfematively we caninciude fhe fwo exsing rooms which wil include
the room with a mezanine floor. Nofe: The client will need fo discuss with
‘council about including these addifional rooms as an amendment fo his
buikding consent or confirm they are happy for these rooms fo be addressed
during the construction monitoring phase of tis project.

It hese fwo rooms are fo be included, an ext sign vl be required
‘above fhe doorinfo fhe office area. (Refer fo Picture B).

= The underside of the mezzanine floor and s supporing stucture fo
it rated fo achieve an FRR 30/30/30. Please nofe fhat fhe lodder
‘may not be compiant f the fravel distance the exceeds a
‘permitied DEOP of 25m. Tnis can be further confiimed once we
have received the updated fioor pian.

Closed.
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