B-203

Code Compliance Summary

| DETAILS |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Property Address: | 80 Byron Street Sydenham |  |  |  |  |  |  |
| Consent Issue Date: | Building Consent Number: |  |  | Project Description: |  |  |  |
| 22/08/2017 10:32:04 AM | BCN/2017/2013 |  |  | Addition to Factory - New Offices, Meeting and Store Room |  |  |  |
| Building level: ☐ R1 ☐ R2 ☐ R3  C1 ☐ C2 ☐ C3 |  |  |  |  |  |  |  |
| Vetting officer: |  | Name: | Tracey Atherton |  | Date Vetting officer Pre-acceptance completeness check started:* |  | 2021-07-19 |
| Property file ordered? |  | ☐ Yes N/A - e-copy in TRIM |  |  | Date Property file ordered (if applicable): |  |  |
| CC Assessor: |  | Name: | Cindy Xia |  | Date CC Assessor process started: |  | 23/07/2021 |
|  |  | Competency: | R1-C3 |  |  |  |  |
| Historic consents process only |  |  |  |  |  |  |  |
| Senior Building Inspector: |  | Name: |  |  | Building Inspector: | Name: |  |
|  |  | Competency: |  |  |  | Competency: |  |
| Risk Level: |  | ☐ Low ☐ High | Reason for level decision: [Note: if a compliance schedule review is required] |  |  |  |  |

|  |  |  |  |  |  |  |  |  | Key for abbreviations to answering processing questions: |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Phone 1st: | Agent |  |  |  |  |  |  | Y | Yes - the application meets the full intent of the question. Provide comment as appropriate. |
|  |  | Owner |  |  |  |  |  |  | N | No - the application does not meet the full intent of the question. Provide comment as appropriate. |
|  |  |  |  |  |  |  |  |  | N/A | Not applicable - the question is not applicable to this application. Provide comment as appropriate. |

Section 1: 	Vetting & Allocation Initial Completeness Check

Section 1a:  	Initial Completeness Check Decision

Section 2: 	Inspections

Section 3: 	Inspection History

Section 4: 	Documentation Summary

Section 5: 	Documentation Summary – Specified Systems

Section 6:	Statement by person(s) with a regulation 18 qualification

Section 7:	Charges

Section 8:	Invoicing / Refunds

Section 9:	Additional Comments

Section 10: 	Final Code Compliance Application Sign Off

Section 11: 	Supervision

Section 12:  	Code Compliance Assessor Final Procedures Checklist

| SECTION 1: VETTING & ALLOCATION INITIAL COMPLETENESS CHECK |  |  |
| --- | --- | --- |
| Application for Code Compliance: All required sections of application form completed and signed? [If owner has changed Certificate of Title is required] | Y | 21/1017547 CD – 16/07/2021 |
| If the proposed building work includes 'restricted building work' has an appropriate 'records of work' been provided for all of the proposed 'restricted building work' by each LBP, Architect or Engineer? [Note received ROWs below and lapse in Connect] | N/A |  |

| Type of Restricted Building Work: |  | LBP Licence Class: | LBP Name and Licence Number: | LBP Rego Current? | TRIM Ref: |
| --- | --- | --- | --- | --- | --- |
| select |  | select |  | ☐ |  |
| select |  | select |  | ☐ |  |
| select |  | select |  | ☐ |  |
| select |  | select |  | ☐ |  |
| select |  | select |  | ☐ |  |
| select |  | select |  | ☐ |  |
| select |  | select |  | ☐ |  |
| select |  | select |  | ☐ |  |
| select |  | select |  | ☐ |  |
| select |  | select |  | ☐ |  |

| Have Energy Certificates been provided? (e.g. House; Heating, Gas) [Lapse in Connect and record HPRM ref] | Y | CDOC-EW01; Energy work certificate - electrical; Accepted; 12 May 2020; TRIM://20/579041; TRIM://20/579041 Accepted - Document(s) can be relied on as author is qualified and holds a current registration - Tracey Atherton - 2020-05-12. |
| --- | --- | --- |

| SECTION 1a: INITIAL COMPLETENESS CHECK decision |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| I confirm that the Vetting & Allocation initial completeness checks have been completed and that the Code Compliance Certificate application is: Accepted |  |  |  |  |  |
| ☐ Not accepted - the reason for non-accepted is: |  |  |  |  |  |
| Signed by the Vetting & Allocation Officer and also confirms that checks are completed and that all relevant information in Section 11 (marked with an *) is contained in the building consent file : |  |  |  |  |  |
|  |  |  |  | Date: | 2021-07-19 |
| Record any previous "Not Accepted" decisions - If n/a please Not Applicable |  |  |  |  |  |
| Date | V&A Officer |  | Reason for non-acceptance |  |  |

| Code Compliance Assessor to complete – insert relevant data from 025 CCC Statement of Compliance: |  |  |
| --- | --- | --- |
| Minor Variations: | Details: |  |
| Minor Variation: BCN/2017/2013. Received date; Decision; Decision date; To be invoiced. 23 Oct 2019; Amendment required; 23 Oct 2019; $0.00. Total Minor Variation processing fee; $0.00. Minor Variation invoiced amount; $0.00. Total to be invoiced; $0.00. |
| Amendments: | Details: |  |
| Amendments: BCN/2017/2013. Consent number; Status; Description. BCN/2017/2013/A; Completed; Amendment 1 - Addition of concrete wall, store room replaced with office space, office partition walls removed, 1 skylight location change, addition of heat pumps, drainage plumbed to sink wastes, hallway extended, interior office windows added, perimeter strip drains reduced to entry doors only, cladding change. BCN/2017/2013/B; Completed; Amendment 2 - change to floor plan, emergency lighting and backflow prevention device. |
| Other Consents: | Details: |  |
| Address related building consents: BCN/2017/2013. Consent number; CCC issued; Status; Description. BCN/1994/3440; 09 Aug 1996; Completed; Sign (hall shopfitting) miscellaneous freestanding sign (hall shopfitting)- Historical Reference CON94003859. BCN/2010/8559; 16 Oct 2013; Completed; REPLACE ROLLER DOOR WITH FIRE WALL- Historical Reference ABA10107578. |
| Section 37 required: Resource Consent Issued | Details: |  |
| Section 37: BCN/2017/2013. Type; Lapsed date; Lapsed; Status. Section 37 Other Consents Required; 13 Apr 2017; Lapsed. |
| Resource Consents: | Details: |  |
| Processing complete |  |  |
| Development Contributions: Paid | Details: DC invoice paid 14/05/2020: DCs of $5,597.90 including GST has been paid.Receipt #248762Kelly**no associated consent** |  |
| Warnings and Bans: No | Details: |  |
| Certificates for Public Use: No | Details: |  |
| Compliance Schedule required: New | BWOF Officer Name: | Ponferrada, Noemi <Noemi.Ponferrada@ccc.govt.nz> |
|  | BWOF Number | WOF56989 |
| General Comments: [Include any applicable Connect memo’s] |  |  |

SECTION 2: INSPECTIONS – insert ‘Inspection status’ and table from 025 CCC Statement of Compliance: [if a Staged Consent, include all tables]

Inspections status: BCN/2017/2013. Inspection type; Description; Result; Date; Status. 210 - Final Inspection; Actual; Pass; 16 Jul 2021. 201 - Pre Pour Foundation; Not required; N/A; 09 May 2019. 203 - Pre Pour Floor; Not required; N/A; 09 May 2019. 205 - Pre Line (Pre Line including Plumbing); Actual; Pass; 21 Nov 2019. 208 - Drainage; Not required; N/A; 21 Nov 2019. 209 - Pre Stop (Pre Stopping); Actual; Pass; 26 Nov 2019. 215 - Building and Sill Wrap or Cavity Batten; Not required; N/A; 24 Sep 2019. 217 - Pre Roof; Actual; Pass; 13 Sep 2019. 221 - Blockwork (Block Work Construction); Not required; N/A; 07 Feb 2020. 251 - Foundation or Slab; Actual; Pass; 22 May 2019. 252 - Drainage; Actual; Pass; 26 Nov 2019. 253 - Pre Cladding; Actual; Pass; 21 Nov 2019. Inspection history: BCN/2017/2013. Click for the Inspection Reconciliation Report. Inspection date; Type; Result; Duration (hrs). 09 May 2019; 201 - Pre Pour Foundation; N/A; 0.00. 09 May 2019; 203 - Pre Pour Floor; N/A; 0.00. 22 May 2019; 251 - Foundation or Slab; Pass; 0.75. 13 Sep 2019; 217 - Pre Roof; Pass; 0.75. 24 Sep 2019; 215 - Building and Sill Wrap or Cavity Batten; N/A; 0.00. 25 Sep 2019; 253 - Pre Cladding; Fail; 1.00. 10 Oct 2019; 205 - Pre Line (Pre Line including Plumbing); Fail; 0.75. 21 Nov 2019; 208 - Drainage; N/A; 0.00. 21 Nov 2019; 205 - Pre Line (Pre Line including Plumbing); Pass; 0.75. 21 Nov 2019; 253 - Pre Cladding; Pass; 0.75. 26 Nov 2019; 252 - Drainage; Pass; 0.75. 26 Nov 2019; 209 - Pre Stop (Pre Stopping); Pass; 0.75. 07 Feb 2020; 210 - Final Inspection; Fail; 0.75. 07 Feb 2020; 221 - Blockwork (Block Work Construction); N/A; 0.00. 11 May 2020; 210 - Final Inspection; Pass; 0.50. 16 Jul 2021; 210 - Final Inspection; Pass; 0.50.

| SECTION 3: INSPECTION HISTORY | Y / N | Comments, Dates, Details |  |
| --- | --- | --- | --- |
| All required inspection types identified as passed: | Y |  |  |
| Total Prepaid Inspections: |  |  |  |
| Total Inspections Completed: |  |  |  |
| Total Fee: | Owing | $ | 255 |
| Additional Comments: [Please list TRIM links to Cost Breakdown information and Inspection Calculations documentation] |  |  |  |
| Modification of durability [Performance requirement B2.3.1] – If N/A please Not Applicable |  |  |  |
| Substantial completion of building work: 16/07/2021 [Refer to audit or final inspection report confirming substantial completion date i.e. month & year] |  |  |  |

| SECTION 4: DOCUMENTATION SUMMARY |  |  |  |
| --- | --- | --- | --- |
| Documentation Status: |  | Action / TRIM link and notes: |  |
| Construction Statement – B-083 |  | Action: Not required |  |
|  |  | TRIM link and Assessor Notes: |  |
| Plumbing – B-084: |  | Action: Accepted by CC assessor |  |
|  |  | TRIM link and Assessor Notes: | TRIM://20/576877 ACCEPTED BCN, address, all complies, signed by Keith Foster, active Plumbing, Reg20315 confirmed, Signed and dated- Cindy Xia15/05/2020 |
| Surveyors Certificate (Siting, HIRB, FFL): |  | Action: Accepted by CC assessor |  |
|  |  | TRIM link and Assessor Notes: | Building location certificate: Provide a B-081 certificate from a registered professional surveyor or a licenced cadastral surveyor. TRIM://20/410836 ACCEPTED BCN and Address, form complete, complies with building consent plans, author adrian cowie, No license number, website envidence, signed and dated - Please check it by inspector - Cindy Xia 30/04/2020 |
| Construction Review (PS4 and Site Inspections): [If applicable, record consultant name] |  | Action: Accepted by CC assessor |  |
|  |  | TRIM link and Assessor Notes: | Construction Monitoring: Provide all site inspection records and a PS4 from your nominated structural consultant [Torlesse Structural] stating that all the necessary aspects of the design has been incorporated into the Building. This includes the following work: · Excavation (subgrade beneath foundation footprint) – by Geotechnical engineer · Foundations before casting · Concrete block walls after reinforcing but before grouting · Structural steelwork after erection · Connections between structural components TRIM://19/1255274 Page 10-12 TRIM://20/128557 ACCEPTED PS4 from Troless Structural Ltd, notes BCN, Amendment number, address, CM3, B1, signed & dated byLong, William Julius CPEng 231242 verified current, site reports attached – Cindy Xia 19/02/2020 |
| Façade inspections (PS4 and Site Inspections): [If applicable, record consultant name] |  | Action: Not required |  |
|  |  | TRIM link and Assessor Notes: |  |
| Drainage Systems (As built): |  | Action: Accepted by CC assessor |  |
|  |  | TRIM link and Notes: | TRIM://20/576877 ACCEPTED As-built plan – Josh Eady, Reg#22552 – Cindy Xia 15/05/2020 |
| Exterior Cladding (PS3): [If applicable, record the system] |  | Action: Not required |  |
|  |  | TRIM link and Notes: |  |
| Membrane – External, e.g., Roof and Decks (PS3): |  | Action: Not required |  |
|  |  | TRIM link and Notes: |  |
| Membrane – Internal, e.g., Shower (PS3): |  | Action: Not required |  |
|  |  | TRIM link and Notes: |  |
| As-built Truss Design: |  | Action: Not required |  |
|  |  | TRIM link and Notes: |  |
| Penetrations through fire separations: |  | Action: Not required |  |
|  |  | TRIM link and Notes: | TRIM://21/1056647 Email from agent:” I can confirm there were no penetrations going thru fire cells in this build.” |
| Intumescent paint: |  | Action: Not required |  |
|  |  | TRIM link and Notes: |  |
| Potable water test certificate (not NUO): [If applicable, record consultant name] |  | Action: Not required |  |
|  |  | TRIM link and Notes: |  |
| On-site disposal systems (PS3): |  | Action: Not required |  |
|  |  | TRIM link and Notes: |  |
| Pressure sewer system (B082): |  | Action: Not required |  |
|  |  | TRIM link and Notes: |  |
| Section 77 Registered: |  | Action: Not required |  |
|  |  | TRIM link and Notes: |  |
| Staged Consent: [If applicable, ensure that the RFI references this] |  | Action: Not required |  |
|  |  | TRIM link and Notes: |  |
| Other: |  | Action: select |  |
|  |  | TRIM link and Notes: |  |
| Other: |  | Action: select |  |
|  |  | TRIM link and Notes: |  |
| Other: |  | Action: select |  |
|  |  | TRIM link and Notes: |  |
| Other: |  | Action: select |  |
|  |  | TRIM link and Notes: |  |
| Other: |  | Action: select |  |
|  |  | TRIM link and Notes: |  |
| Other: |  | Action: select |  |
|  |  | TRIM link and Notes: |  |
| Other: |  | Action: select |  |
|  |  | TRIM link and Notes: |  |
| Notes: |  |  |  |
| Only the above producer statements have been considered for reliance. If other producer statements have been provided voluntarily, they will be saved in the consent file in TRIM, but not reviewed or relied upon. |  |  |  |

| SECTION 5: DOCUMENTATION SUMMARY – SPECIFIED SYSTEMS – If n/a please select |  |  |  |
| --- | --- | --- | --- |
| Documentation Status: |  | Action / TRIM link / Notes: |  |
| 1 Automatic systems for fire suppression: - (PS3): |  | Action: Not required |  |
|  |  | TRIM link and Notes: |  |
| - (Certificate of Compliance): |  | Action: Not required |  |
|  |  | TRIM link and Notes: |  |
| 2 Automatic or manual emergency warning systems for fire or other dangers: - (PS3): |  | Action: Not required |  |
|  |  | TRIM link and Notes: |  |
| - (Certificate of Compliance): |  | Action: Not required |  |
|  |  | TRIM link and Notes: |  |
| 3/1) Automatic doors: |  | Action: Not required |  |
|  |  | TRIM link and Notes: |  |
| 3/2) Access control doors: |  | Action: Not required |  |
|  |  | TRIM link and Notes: |  |
| 3/3) Automatic fire doors: |  | Action: Not required |  |
|  |  | TRIM link and Notes: |  |
| 4 Emergency lighting systems (PS3) |  | Action: Accepted by CC assessor |  |
|  |  | TRIM link and Notes: | TRIM:// 21/1015483 ACCEPTED PS3 EML, address, BCN, description and scope acceptable, Code clauses F6, F8, indicated, relevant qualification given E257447 signed by Tim Davies dated 20/05/2020 – Cindy Xia15/05/2020 |
| 4 Emergency lighting systems (PS4) |  | Action: Accepted by CC assessor |  |
|  |  | TRIM link and Notes: | Emergency lighting - with PS4 for F6 from Cosgroves PS1 AMENDMENT 2 - TRIM://20/801376 TRIM:// 21/1056647 ACCEPTED PS4 from Cosgroves Ltd, notes BCN, Amendment A,B address, CM2, F6 & F8 (Part), signed & dated by Stephen Page CPEng 216143 verified current – Cindy Xia 27/07/2021 |
| 5 Escape route pressurisation systems: |  | Action: Not required |  |
|  |  | TRIM link and Notes: |  |
| 6 Hydrant System/Riser mains: |  | Action: Not required |  |
|  |  | TRIM link and Notes: |  |
| 7 Automatic backflow preventers connected to potable water supply: |  | Action: Accepted by CC assessor |  |
|  |  | TRIM link and Notes: | TRIM:// 21/1015483 ACCEPTED IQP Test report. Address, Location: Service office, make Apollo, size: 20mm, Model number: DCAUCF4A, Serial #985136, Signed by IQP 886 Matt Boot confirmed dated 13/07/2021 – Cindy Xia 23/07/2021 |
| 8/1, 8/2, 8/3 Lifts, Escalators, travelators, or other systems for moving people within buildings: |  | Action: Not required |  |
|  |  | TRIM link and Notes: |  |
| 9 Mechanical ventilation or air conditioning systems (HVAC): |  | Action: Accepted by CC assessor |  |
|  |  | TRIM link and Notes: | TRIM:// 21/1016728 ACCEPTED HVAC As-built plan – Cindy Xia 23/07/2021 TRIM://20/576877 ACCEPTED PS3 HVAC, address, BCN, description and scope acceptable, Code clauses G4,indicated, relevant qualification givenE257447 signed by Tim Davies dated29/01/2020 – Cindy Xia15/05/2020 |
| 10 Building maintenance units providing access to the exterior and interior walls of buildings: |  | Action: Not required |  |
|  |  | TRIM link and Notes: |  |
| 11 Laboratory fume cupboards: |  | Action: Not required |  |
|  |  | TRIM link and Notes: |  |
| 12/1, 12/2 Auto loops or other assistive listening systems: |  | Action: Not required |  |
|  |  | TRIM link and Notes: |  |
| 13/1, 13/2 Natural/Mechanical smoke control systems, smoke curtains: |  | Action: Not required |  |
|  |  | TRIM link and Notes: |  |
| 14/1) Emergency power systems: |  | Action: Not required |  |
|  |  | TRIM link and Notes: |  |
| 14/2) Signs relating to, a system or feature specified in any of clauses above: |  | Action: Accepted by CC assessor |  |
|  |  | TRIM link and Notes: | Checked by final inspection -TRIM:// 21/1015483 Accepted Photos for no storage above 3M. |
| 15/1) Systems for Communicating spoken information intended to facilitate evacuation: |  | Action: Not required |  |
|  |  | TRIM link and Notes: |  |
| 15/2) Final exits(as defined by clause A2 of the Building Code); and |  | Action: Accepted by CC assessor |  |
|  |  | TRIM link and Notes: | Checked by final inspection |
| 15/3) Fire separations (as so defined); and |  | Action: Not required |  |
|  |  | TRIM link and Notes: |  |
| 15/4) Signs for communicating information intended to facilitate evacuation; and |  | Action: Accepted by CC assessor |  |
|  |  | TRIM link and Notes: | Checked by final inspection |
| 15/5) Smoke separations (as so defined): |  | Action: Not required |  |
|  |  | TRIM link and Notes: |  |
| Fire Engineer PS4: |  | Action: Accepted by CC assessor |  |
|  |  | TRIM link and Notes: | TRIM:// 21/1015483 ACCEPTED PS4 from FireForce Ltd notes BCN, Amendment A, address, CM2, C3, C4, signed & dated by Will Tsai CPEng 1011344 verified current, site reports attached – Cindy Xia 23/07/2021 TRIM://20/576877 ACCEPTED Letter from FireForse – inspection records – Cindy Xia 15/05/2020 |
| Other: |  | Action: select |  |
|  |  | TRIM link and Notes: |  |
| Other: |  | Action: select |  |
|  |  | TRIM link and Notes: |  |
| Other: |  | Action: select |  |
|  |  | TRIM link and Notes: |  |
| Other: |  | Action: select |  |
|  |  | TRIM link and Notes: |  |
| Other: |  | Action: select |  |
|  |  | TRIM link and Notes: |  |
| Other: |  | Action: select |  |
|  |  | TRIM link and Notes: |  |
| Compliance Schedule Review: |  |  |  |
| Completed |  |  |  |
| Documentation Notes: |  |  |  |
| 2021-07-29 – CS review completed. All documentations were supplied. CS and CSS issued under WOF/2020/5827. |  |  |  |
| Only the above producer statements have been considered for reliance. If other producer statements have been provided voluntarily, they will be saved in the consent file in TRIM, but not reviewed or relied upon. |  |  |  |

| SECTION 6: STATEMENT BY PERSON(S) WITH A REGULATION 18 QUALIFICATION |  |
| --- | --- |
| I have reviewed and verified the above construction documentation (Section 4 and Section 5), and I am satisfied they demonstrate the building work complies with the building consent. |  |
| # Notes: I have reviewed the auditor’s notes in regards to received documentation and I believe that ccc can now be issued. | Signature(s): Jacob Burns Acting Senior Building Inspector |

| SECTION 7: CHARGES |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Notice to Fix - | n/a |  | occurrences: |  |  |  |  | $ |  |
| CCC Building Inspections |  |  |  | 21/1045411 |  | occurrences: |  | $ | 255 |
| Code Compliance Re Application Fee (S95): |  |  |  |  |  |  |  | $ |  |
| Code Compliance Additional processing |  |  |  |  | 21/1059808 |  |  | $ | 628.30 |
| Reminder: Include 30 minutes additional processing time for issuing the Code Compliance Certificate Include 60 minutes additional processing time for issuing the Compliance Schedule |  |  |  |  |  |  |  |  |  |
| Minor Variation |  | n/a |  | occurrences: |  |  |  | $ |  |
| Amendment to modify building code clause B2 – Durability (deposit) |  | n/a |  |  |  |  |  | $ |  |
| Other: |  | n/a |  |  |  |  |  | $ |  |
| Total Fees Outstanding * Code Compliance must be issued before Refunds are processed * Funds owed/refunded may be adjusted in the event of a failed final inspection |  |  |  |  |  |  |  | $ | 883.20 |
| Additional Comments: [Please list TRIM links to any additional Chargeable Services and Processing Reconciliation documentation] |  |  |  |  |  |  |  |  |  |

| SECTION 8: INVOICING / REFUNDS |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Invoice / Credit Note Number: | Amount: | Type: | Date Sent: | Sent to: | Date Paid: | TRIM Ref: [Insert TRIM link to Invoice / Credit Note] |
| 219631 | $883.20 | Inspection (additional) CCC additional | 27/07/2021 | AGENT | 02/08/2021 |  |

SECTION 9: ADDITIONAL COMMENTS

Officer’s Note:

| SECTION 10: FINAL CODE COMPLIANCE APPLICATION SIGN OFF |  |
| --- | --- |
| Matters for consideration by building consent authority in deciding to issue a code compliance certificate DECISION – Select yes if you agree, or no if you disagree with the applicable statement below. Select N/A for the statement that is not applicable Yes : Section 94 (for building consents granted under the Building Act 2004) On the basis of the satisfactory completion of inspections and that all the construction documentation requested with the building consent has been provided and verified by a person with a regulation 18 qualification, I, on behalf of the Christchurch City Council, am satisfied on reasonable grounds that the building work complies with the building consent and that in a case where a compliance schedule (or an amendment to an existing compliance schedule) is required as a result of the building work, the specified systems in the building (or that are being altered in, or added to, the building in the course of the building work) are capable of performing to the performance standards set out in the building consent. Consideration also has been made that the requirements of section 94 (2), (3) and (4) have been met. OR N/A : Section 436 (for building consents granted under the Building Act 1991) On the basis of the satisfactory completion of inspections and that all the construction documentation requested with the building consent has been provided and verified by a person with a regulation 18 qualification, I, on behalf of the Christchurch City Council, am satisfied that the building work concerned complies with the building code that applied at the time the building consent was granted. |  |
| Issue of code compliance certificate or refusal to issue code compliance certificate Yes : Section 95 Issue of code compliance certificate On the basis of the decision above the code compliance certificate must be issued by Christchurch City Council on the prescribed form on payment of any fees and charges imposed by the building consent authority under section 219 or 240. OR N/A : Section 95A Refusal to issue code compliance certificate On the basis of the decision above the Christchurch City Council refuses to issue a code compliance certificate, and must give the applicant written notice of the refusal; and the reasons for the refusal. |  |
| Name: | Cindy Xia |
| Date: | 02/08/2021 |
| Select option above (issue or refusal) and sign: |  |
|  | Signature: Weiwei Xia. Code Compliance Assessor. 02/08/2021 12:44 pm. |

| SECTION 11: SUPERVISION - If n/a please Not Applicable |  |  |
| --- | --- | --- |
|  | Comments: |  |
| # Record details of supervision by competent Code Compliance Assessor where building category is above or outside Assessor's competency level. Provide competent officer’s name and date of ‘sign-off’. |  |  |
|  | Signature: |  |

| SECTION 12: CODE COMPLIANCE ASSESSOR FINAL PROCEDURES CHECKLIST: CONFIRMATION THAT ALL RELEVANT INFORMATION IS CONTAINED IN THE BUILDING CONSENT FILE | Located: Y / N / NA |
| --- | --- |
| * B-011 Application for Code Compliance Certificate (Form 6) | Y |
| * Record of Work(s) by licensed building practitioners (Form 6A, B, C) | N/A |
| * Energy works certificates | Y |
| B-013 Application for Certificate for Public Use (Form 15) | N/A |
| B-450 Certificate for Public Use (Form 16) | N/A |
| B-440 Notice to Fix (Form 13) | N/A |
| B-460 Compliance Schedule statement (building warrant of fitness) (Form 10) | N/A |
| B-461 Section 1 Compliance Schedule | N/A |
| Dangerous/EQ prone/Insanitary Building notices (section 124 notices) | N/A |
| Producer statement construction (PS3) / Producer statement construction reviews (PS4) | Y |
| Inspections records and evidence | Y |
| Minor variation documentation | N/A |
| Summary of written complaints | N/A |
| B-006 Application for amendment to building consent for modification of durability periods to clause B2.3.1 | N/A |
| B-410 amended building consent subject to a modification of B2.3.1 | N/A |
| B-140 Notification of Waiver or Modification of the Building Code | N/A |
| Copy of invoices | N/A |
| All email/letter/faxed correspondence relative to the individual consent | Y |
| Staged building consents – All stages completed | Y |
| B-451 Code Compliance Certificate (Form 7) | Y |
| Final Task Checklist: |  |
| Have all workflows been completed in connect and final administration completed | Y |
| All CCC documents have been converted to PDFs | Y |
| All building consent file documents are made 'public' and 'finalised' | Y |
| If the application is commercial structural strengthening/upgrade related, email a copy of the B451 and relevant PS4 to DEEs@ccc.govt.nz | N/A |
| If the application includes a pressure sewer system, email the BCN, address and As-Built drainage trim reference to asset.handover2@ccc.govt.nz | N/A |

| Confirmed by the Code Compliance Assessor that all relevant information in Section 11 (not marked with an *) is contained in the building consent file: |  |
| --- | --- |
| Name: | Cindy Xia |
| Date: | 02/08/2021 |