| 13 May 2020 Spaghetti Junction Limited 210 Huntsbury Avenue Huntsbury Christchurch 8022 | 03 941 8999 53 Hereford Street Christchurch 8011 PO Box 73013 Christchurch 8154 ccc.govt.nz |
| --- | --- |

Dear  John,

Compliance schedule and statement.

WOF56989

80  Byron Street

We are pleased to confirm your compliance schedule and statement can be issued together with your code compliance certificate. Please refer to the schedule for the specified systems and features, and required inspection, maintenance and reporting.

If you would like to talk to us, or if you think that the systems / features on the schedule do not reflect those in the building, you can contact me on the number below or email buildingwof@ccc.govt.nz.

In a year’s time you will need to send us a signed copy of your Building Warrant of Fitness, along with a copy of the relevant Certificates of Compliance. You need to engage an agent / IQP (Independent Qualified Person) to do the inspection, maintenance and reporting.

Please refer to sections 105, 108 and 110 of the Building Act for more information on owner’s obligations. legislation.govt.nz/act/public/2004/0072/latest/DLM306866.html

The compliance statement will need to be displayed in a public area of the building. The compliance schedule must be kept at the address referred to in the statement.

Yours sincerely,

Noemi Ponferrada

Building Officer - Warrant of Fitness

Building Consenting Unit

Direct Dial 03 941 5074

Compliance Schedule Statement

Section 105, Building Act 2004

### Form 10 – Building (Forms) Regulations 2004

### Compliance Schedule No: WOF56989

Date Issued: 13 May 2020	Expiry Date: 1 May 2021

The building

Street address of building:

80  Byron Street

Building name: Clip N' Climb Factory

Level/Unit number: Single

Location of building within site/block number:

Year building first constructed: Unknown

Currently, lawfully established, use (in detail) and any conditions of use: Commercial: Factory, Office, Store Areas (3m Max. Signage Requried)

Occupant numbers: 16
Use(s) (as per Schedule 2, Building Regulations 2005): WL:WM:

Highest fire hazard category: FHC 3

Life of building stated in years:      
(if less than 50 years)

Legal description:

LOT 1 DEPOSITED PLAN 449853

The owner

Name of owner:  Spaghetti Junction Limited

Contact person:(if owner not an individual)

Mailing address:                                                                          210 Huntsbury Avenue                                                            Huntsbury                                                                           Christchurch 8022

Street address/registered office:

Phone numbers:

Landline:	 Mobile: 0212213080

Daytime:	After hours:

Fax:

Email:  jt@clipnclimb.com

Website:

Specified systems

The following specified systems are covered by the compliance schedule for this building: (list appropriate system(s))

4	Emergency Lighting System

7	Automatic Backflow Prevention Connected to Potable Water Supply

15/2	Final exit (as defined by A2 of the Building Code)

15/4	Signs for communicating information intended to facilitate evacuation.

The Compliance Schedule is kept at: 80 Byron Street

Signature:

Position:   Building Officer – Warrant of Fitness

On behalf of:  Christchurch City Council

Date: 13 May 2020

This statement is valid until 1 May 2021.

Compliance Schedule

issued in accordance with SECTION 100, BUILDING ACT 2004

Compliance Schedule Number: WOF56989	BWOF Renewal Date: 1 May

The building

Property ID: 921510

| Street address of building: 80 Byron Street Building name: Clip N' Climb Factory Level/Unit number: Single Location of building within site/block number: Year building first constructed: Unknown Currently, lawfully established, use (in detail) and any conditions of use: Commercial: Factory, Office, Store Areas (3m Max. Signage Requried) |  | Occupant numbers: 16 Use(s) (as per Schedule 2, Building Regulations 2005): WL:WM: Highest fire hazard category: FHC 3 Life of building stated in years: (if less than 50 years) Legal description: LOT 1 DEPOSITED PLAN 449853 |
| --- | --- | --- |

The owner

Owners ID:  4106179

| Name: Spaghetti Junction Limited Owner contact: Mailing address: 210 Huntsbury Avenue Huntsbury Christchurch 8022 |  | Phone number: Mobile: 0212213080 Email address: jt@clipnclimb.com Fax: Website: |
| --- | --- | --- |

The reporting procedures

- Log books must be kept and maintained confirming the inspections, as applicable to each Specified System, have been carried out by the individuals responsible for inspecting and maintaining the systems or features (including but not limited to Owners, Service Technicians and Independent Qualified Persons).

- Where a Specified System is listed on this Compliance Schedule, only one Form 12A is to be provided by a Independently Qualified Person for that particular system, confirming all the required procedures have been undertaken.

Notes:

- This Compliance Schedule forms the specifications for the features contained in or attached to the building known as the Specified Systems.

- It is the Building Owners’ responsibility to ensure the Specified Systems are maintained and reported on according to the Inspection, Maintenance and Reporting Procedures of this Compliance Schedule.

- Inspection, Maintenance and Reporting Procedures must be checked against the latest fire safety summary for the building.

- Where information is not available, or listed on this Compliance Schedule, it is the Building Owners’ responsibility to maintain and operate the building in compliance with the Building Act 2004 and associated compliance documents.

- To request amendments to this Compliance Schedule provide a “Request to Amend Compliance Schedule” (Form 11) to Christchurch City Councils’ Building Warrant of Fitness team.

- It is the Owners responsibility to make this Compliance Schedule available to anyone who has the right to inspect buildings and provide a copy to all service agents.

- Form 12a’s for all systems or features are to be provided along with the annual Building Warrant of Fitness (Form 12) for the building.

The specified systems

| Specified System 4 |  |  | Emergency lighting systems |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Description: Type: | Emergency Lighting System Systems installed from 1995 complying with AS/NZS 2293 Part 1, 2 and 3 |  |  |  |  |  |  |  |  |  |  |  |
| Location, Make (if known), Model number (if known): | Location: At changes in levels, and escape routes where required by F6/AS1 Make and model: Ektor – self contained, non-maintained |  |  |  |  |  |  |  |  |  |  |  |
| Maintenance Procedure Performance Standards |  | As specified by AS/NZS 2293 Part 2:1995 |  |  |  |  |  |  |  |  |  |  |
| Inspection Frequency |  |  |  |  |  |  |  |  |  | 6 Monthly |  | Annually |
| Maintained or Inspected By |  |  |  |  |  |  |  |  |  | Independent Qualified Person |  | Independent Qualified Person |
| Specified System 7 |  |  |  | Automatic backflow preventers connected to a potable water supply |  |  |  |  |  |  |  |  |
| Description: Type: | Automatic Backflow Preventer Connected to Potable Water Supply complying with AS 2845:1998 Part 3 |  |  |  |  |  |  |  |  |  |  |  |
| Location, Make (if known), Model number (if known): | Location: Service Office – 78 Byron Street Make and model: Apollo, DCAULF4A, 20mm Serial number: 985136 |  |  |  |  |  |  |  |  |  |  |  |
| Maintenance Procedure Performance Standards |  | As specified by AS 2845:1998 Part 3 |  |  |  |  |  |  |  |  |  |  |
| Inspection Frequency |  |  |  |  |  |  |  |  |  |  |  | Annually |
| Maintained or Inspected By |  |  |  |  |  |  |  |  |  |  |  | Independent Qualified Person |
| Specified System 15/2 |  |  |  |  | Final exits (as defined by clause A2 of the Building Code) |  |  |  |  |  |  |  |
| Description: Type: | Final exit doors |  |  |  |  |  |  |  |  |  |  |  |
| Location, make, model number (if known): | Location: All final exit points on escape routes giving direct access to a safe place Make and model: Unknown |  |  |  |  |  |  |  |  |  |  |  |
| Performance standards and reference for inspection maintenance and reporting procedures |  | Performance standards to paragraph 3.15 of the acceptable solutions C/AS2 (2019) Inspections and maintenance procedures in accordance with the details on pages 49 - 50 in the Ministry of Business, Innovation and Employment Compliance Schedule Handbook, Amendment 3 |  |  |  |  |  |  |  |  |  |  |
| Inspection Frequency |  |  |  |  |  |  | Monthly |  |  |  |  | Annually |
| Maintained or Inspected By |  |  |  |  |  |  | Owner |  |  |  |  | Independent Qualified Person |

| Specified System 15/4 |  |  | Signs for communicating information intended to facilitate evacuation |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Description: Type: | Exit and other signs for communicating information intended to Facilitate Evacuation |  |  |  |  |  |  |  |
| Location, Make (if known), Model number (if known): | Location: At final exits and escape routes Make and model: Illuminated Exits signs – Ektor, self contained, maintained |  |  |  |  |  |  |  |
| Maintenance Procedure Performance Standards |  | All signs are to be clearly visible and unobstructed. Signs shall be refurbished before they become illegible, and shall be replaced immediately should they be missing. Defects in illuminated signs shall be replaced immediately they are apparent. And in accordance with Compliance Document F8/AS1. |  |  |  |  |  |  |
| Inspection Frequency |  |  |  |  | Monthly |  |  | Annually |
| Maintained or Inspected By |  |  |  |  | Owner |  |  | Independent Qualified Person |

The history

Original date of issue: 	13 May 2020

Amendment by:		Building Consent, BCN/2017/2013 – Addition to Factory – New Offices, Meeting and Store Room

Attachments include:       Indicative Fire Drawing and Emergency Lighting Layout – BCN/2017/2013

Signed for and on behalf of Christchurch City Council:

Name:		Noemi Ponferrada

Position:	Building Officer – Warrant of Fitness

Date:		13 May 2020