Compliance Schedule

ISSUED IN ACCORDANCE WITH SECTION 100, BUILDING ACT 2004

Compliance Schedule Number: WOF/2020/5827             		BWOF Renewal Date: 1 August

 (
The building
)
	

	Street address of building: 
80 Byron Street, Sydenham, Christchurch
Building name: 

Level/Unit number: 	Single 

Location of building within site/block number:  

Year building first constructed: 	Unknown

Currently, lawfully established, use (in detail): 	Commercial: Factory, Office, Store Areas
Conditions of use: 	No Storage above 3.0m in warehouse/workshop - signage required 

	





	Occupant numbers: 	16

Use(s) (as per Schedule 2, Building Regulations 2005): 	Working Low 2	Working Medium 

Highest fire hazard category: 	FHC3 

Life of building stated in years: 
(if less than 50 years)

Legal description:
Lot 1 DP 449853


 (
The owner
)

	

	Name: NBA Christchurch One Limited
Owner contact: Nicholas Ash




Mailing address:  
80 Byron Street
Sydenham 
Christchurch 8023
	
	Phone number:  
Mobile: 027 443 7955 
Email address:  
Website:



 (
The reporting procedures
)



1. Log books must be kept and maintained confirming the inspections, as applicable to each specified system, have been carried out by the individuals responsible for inspecting and maintaining the systems or features (including but not limited to owners, service technicians and independent qualified persons).
2. Where a specified system is listed on this compliance schedule, only one Form 12A is to be provided by an independently qualified person for that particular system, confirming all the required procedures have been undertaken.

Notes:
1. This compliance schedule forms the specifications for the features contained in or attached to the building known as the specified systems.
2. It is the building owners’ responsibility to ensure the specified systems are maintained and reported on according to the inspection, maintenance and reporting procedures of this compliance schedule.
3. Inspection, maintenance and reporting procedures must be checked against the latest fire safety summary for the building.
4. Where information is not available, or listed on this compliance schedule, it is the building owners’ responsibility to maintain and operate the building in compliance with the Building Act 2004 and associated compliance documents.
5. To request amendments to this compliance schedule provide an “Application for amendment to a compliance schedule” (Form 11) to Christchurch City Councils’ Building Warrant of Fitness team.
6. It is the owner’s responsibility to make this compliance schedule available to anyone who has the right to inspect buildings and provide a copy to all service agents.
7. Form 12A’s for all systems or features are to be provided along with the annual Warrant of fitness (Form 12) for the building.
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 (
Specified systems
)




	Specified System 4
	Emergency lighting systems

	System description: 
	Emergency lighting system to AS 2293 Part 1 and 3

	Location(s):
	At changes in levels, and escape routes where required by F6/AS1

	Make and model (if known):
	Ektor – self-contained, non-maintained

	Performance standards:
	AS 2293: Parts 1 and 3:2005 as amended by Appendix B, F6/AS1

	Inspection, maintenance and reporting procedures:
	AS/NZS 2293 Part 2:1995.

	Frequency of inspections:
	
	
	
	6-Monthly
	Annually

	Maintained and inspected by:
	
	
	
	Independent Qualified Person
	Independent Qualified Person



	Specified System 7
	Automatic backflow preventers connected to a potable water supply

	System description: 
	Automatic backflow preventer to AS/NZS 2845.1 connected to potable water supply  

	Location(s):

	Service Office – 78 Byron Street

	Make and model (if known):
	Apollo, DCAULF4A, 20mm  

	Serial number:
	985136

	Performance standards:
	AS/NZS 2845.1:2010

	Inspection, maintenance and reporting procedures:
	Field testing and maintenance of testable devices as specified by AS 2845.3:2010 and NZ backflow testing standard 2011

	Frequency of inspections:
	
	
	
	
	Annually

	Maintained and inspected by:
	
	
	
	
	Independent Qualified Person



	Specified System 15/2
	Final exits (as defined by clause A2 of the Building Code)

	System description: 
	Final exit doors

	Location(s):
	All final exit points on escape routes giving direct access to a safe path

	Make and model (if known):
	Unknown

	Performance standards:
	Paragraph 3.15 of the acceptable solutions C/AS2 (2019)

	Inspection, maintenance and reporting procedures:
	Inspections and maintenance procedures in accordance with the details on pages 49 - 50 in the Ministry of Business, Innovation and Employment Compliance Schedule Handbook, Amendment 3

	Frequency of inspections:
	
	Monthly
	
	
	Annually

	Maintained and inspected by:
	
	 
Owner 

	
	
	Independent Qualified Person



	Specified System 15/4
	Signs for communicating information intended to facilitate evacuation

	System description: 
	Signs at all final exit points and throughout escape routes

	Location(s):
	Exit signage - throughout the escape routes and at the final exits
Storage limitation signage (3m max.) - as detailed in the Fire Engineering Report by Cosgroves, dated 7/11/16, Ref: 16175 RevB

	Make and model (if known):
	Illuminated Exit Signs - Unknown

	Performance standards:
	Building code performances F8.3.1, F8.3.2 and F8.3.3

	Inspection, maintenance and reporting procedures:
	Inspection and maintenance procedures to ensure all signs are of the correct type, present in the right locations, legible, clearly visible and unobstructed. Signs shall be refurbished before they become illegible, and shall be replaced immediately should they be missing. Defects in illuminated signs shall be replaced immediately they are apparent.

	Frequency of inspections:
	
	Monthly
	
	
	Annually

	Maintained and inspected by:
	
	
Owner
	
	
	Independent Qualified Person






 (
The history
)


Original date of issue:	02 August 2021
Issued by	Building Consent – BCN/2017/2013 
Addition to Factory – New Offices, Meeting and Store Room

Amendment date: 	26 October 2021
Amendment by:	Territorial Authority – Change of Owner

Attachments include:  	BCN/2017/2013 - Indicative Fire Drawing 
BCN/2017/2013 - Emergency Lighting Layout

Signed for and on behalf of Christchurch City Council:
	



Name:		Lisa Kupenga	
Position:	Building Officer - Warrant of Fitness
Date:		26 October 2021
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